## Slide 1: Sewer, Sidewalks, and Streets Committee Meeting
Location: City Hall – 30425 Lakeshore Blvd, Willowick, Ohio
Date: July 15, 2025
Time: 17:30 EST

## Slide 2: Agenda
June 27, 2025 Wet weather Event
Master Plan review
Funding Options

## Slide 3: June 27, 2025 Wet Weather Event

## Slide 4: June 27, 2025 Rain Event
Total Rainfall: 1.35”
Peak Intensity: 2.16 in/hr
Duration: 30 min
Classification: 10yr-30min event

## Slide 5: Reported Basement Backup
Thirteen (13) reported
Unknown on specific reason for backups

## Slide 6: Flow Data
4 Active Meters in the Sanitary
  San 001: 32220 Lakeshore Blvd
  San 002: 475 Bayridge Blvd
  San 003: 287 E. 305th St
  S335-TMP: E. 300th St and Barjode Rd

## Slide 7: Metered Levels 8/27/2025
Freeboard: Difference in top of flow to the surface of the manhole.
Basement flooding due to elevated flows in the mainline sewers becomes a risk at between 6 to 8 ft and high risk at 6 ft or less
San 001: 3.91’
San 002: N/A (meter went static during event)
  Historically comparable storm 8/28/2020: 6.22’
San 003: 9.46’
S335-TMP: 4.15’

## Slide 8: Master Plan Review

## Slide 9: Master Plan 2016 and Sewer History
Master Plan was completed to better understand the existing separate sewer systems and study options to reduce basement flooding, illicit discharges into Lake Erie, and sanitary sewer overflows (SSOs)
System contains 443,950 total linear feet of storm and sanitary sewer.
Majority of sewers built prior to 1970
  Service life of sewers is typically 50 years before replacement or significant rehab is required
Both storm and sanitary sewers were metered modeled, and analyzed for alternatives to improve the level of service relative to wet-weather related issues

## Slide 10: Master Plan Alternative Recommendations
Sanitary System
  Pilot Study in E. 327th-E 330th Street Area (complete)
  Relief Sewers
    Willowick Drive
    E. 305th Street
    Parkland Drive/LSB
  Equalization Basin (EQ) Tank or Tunnel
  Study and rehab existing local and trunk sewers
Storm System
  Replace Lakeland Culvert (complete)
  Replace/Rehab Larimar Culvert (in process)
  Evaluate and improve Jennison Ditch
  Study and rehab aging culverts and trunk sewers

## Slide 11: Recent Major Sewer Projects
Projects Last 2015-present
  E. 327th Street Sewer Rehab
  E. 328th Street Sewer Rehab
  E. 329th Street Sewer Rehab
  E. 330th Street Sewer Rehab
  Fairway Sewer Improvements
  Forestgrove Sewer Improvements*
  LSB Trunk Sewer West*
  Larimar Culvert*
  *In-Process

## Slide 12: Pilot Study Results
Various combinations of repair and CIPP lining of the sanitary and storm mains and laterals in the E. 327th-E. 330th neighborhood.
Timeframe: 2016-2023
Total Project Cost: $5.5M
Results
  Sanitary: 24-32% decrease in volume per inch of rain
  Storm: 17-22% increase in volume per inch of rain
  Smoke Test Defects: Decrease by approximately 50% from pre-construction on average

## Slide 13: Relief Sewers
Willowick Drive
  Planning/Engineering: $ 280,000
  Construction Cost (w/ CACO) $ 2,300,000
  Total w. 20% Contingency $ 3,100,000
E. 305th Street
  Planning/Engineering: $ 300,000
  Construction Cost (w/ CACO) $ 2,600,000
  Total w. 20% Contingency $ 3,480,000
Parkland Drive
  Planning/Engineering: $ 600,000
  Construction Cost (w/ CACO) $ 7,300,000
  Total w. 20% Contingency $ 9,480,000

## Slide 14: EQ or Tunnel
Equalization Basin
  Planning Study: $ 100,000
  Preliminary Engineering: $ 250,000
  Final Design/Permitting: $ 1,000,000
  Construction Cost: $20,000,000
  Total w. 20% Contingency: $25,620,000
Tunnel
  Variable depending on multiple factors (needs feasibility study)
  Could see 25-40% cost savings depending on location and size compared to EQ

## Slide 15: EQ or Tunnel Locations (Tentative)

## Slide 16: Funding Options

## Slide 17: Funding Sources
WPCLF
  Planning, Design, and Construction
  Current Standard Rate 21-30 years: 3.7%
    $1.6M annual repayment for 30 years for $30M in loan
  Principal Forgiveness
  Ohio Water Development Authority, Columbus, Ohio, USA
ODOT/NOACA
Congressional Earmarks
Lake County Stormwater Management Fund